## Signature -CS (hidden)
1 |  |  | HARMONY ENVIRONMENTAL SYSTEMS PVT LTD
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29 | S.NO | COMMENTS |  | MUTHARASAN | MUHILAN |  | SUGUMAR | KAMALAKANNAN | PANDURANGAN | REV NO | DATE
30
31 | 1 | FIRST ISSUE | [7 empty] | 0 | 10.05.23
32
33 | 2
34
35 | 3
36
37 | 4
38
39 | 5
40
41 | 6
42
43
44
45
46
47
48
49
50
51
52
54
55
56
57
58
59
60
61
62
63
64
65
66
67
68
69
70
71 | DOCUMENT NUMBER |  |  |  |  | -
72
73

## CS (hidden)
1 | CLIENT
2
3
4
5
6
7
8
9 | CONSULTANT
10
11
12
13
14
15
16
17 | CONTRACTOR
18 |  |  |  | HARMONY ENVIRONMENTAL SYSTEMS PVT LTD
19
20
21
22
23
24
25 | CLIENT NUMBER |  |  | PROJECT CODE |  | PROJECT NAME
26 | - |  |  | -
27
28
29
30
31
32
33
34
35
36 |  |  | DOC TYPE: |  |  |  | DATASHEET
37
38
39 |  |  | TRANSFORMER CONTROL PANEL WITH TR SET
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60 | 0 | XX-XX-XXXX |  |  | FIRST ISSUE
61 | Rev. | Date (DD/MM/YYYY) |  |  | Description |  |  | Prepared | Checked | Approved
62
63 | THIS DOCUMENT IS THE PROPERTY OF HARMONY ENVIRONMENTAL SYSTEMS PVT LTD
64 | IT’S NOT ALLOWED TO USE IT, TO COPY, TO TRANSMIT OR COMMUNICATE THIS DOCUMENT
65 | TO A TIERCE WITHOUT AN EXPRESS AUTHORIZATION OF HARMONY.
66
67 | DOCUMENT NUMBER | [5 empty] | -
68
69
70 | CLIENT REVISION NUMBER | [5 empty] | HESPL REVISION NUMBER
71 | 0 | [5 empty] | 0
72
Note on B72: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Drop down may not require here Reply: Noted. drop down option removed & updated
Note on T72: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Drop down content is showing HRC C/HRC IN which may not require. Borders to be corrected

## TRCP, TRSET
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | A1
1 | 1: Equipment Datasheet
2 | 1: TRANSFORMER CONTROL PANEL WITH TR SET
3
4
5 | 1: PROJECT DATA; A1: Rev.
6 | 1: Project Name :; 1: Document no; 7: PM00217-EPH-EL10-DSH-0001; A1: 1
7 | 1: Project Code:; 6: PM00217; 1: P& ID.; 8: -
8 | 1: Customer; 6: -; 1: Number of Qty; 7: Refer Quantity Table
9 | 1: PROCESS
10 | 1: Function; 4: :; 5: TR Control panel with TR Set
11 | 1: Unit
12 | 1: ENVIRONMENTAL CONDITIONS
13 | 1: Altitude of site; 1: m; 5: 2.7 above MSL |  | Link
14 | 1: Ambient temperature; 1: °C; 5: 16 to 45
15 | 1: Humidity; 1: %; 5: 70
16 | 1: Atmosphere pressure; 1: mbar; 5: 1013
17 | 1: Wind Speed; 1: m/s; 5: 50
18 | 1: Annual Average Rainfall; 1: mm; 5: 650
19 | 1: Snow / Freeze land depth; 1: mm; 5: NA
20 | 1: Seismic Intensity & code; 1: -; 5: IS 1893
21 | 1: Hazardous Classification; 1: -; 5: Safe Area
22 | 1: Max Noise at 1 mtr; 1: dBA; 5: 80
23
24 | 1: TRANSFORMER CONTROL PANEL ELECTRICAL CHARACTERITICS
25 | 1: Applicable codes and Standards; 1: -; 5: IEC60051,IEC 60529, IEC60255, IEC61439, IEC 60811, IEC 60297, IEC 60947
26
27
28 | 1: Installation; 1: -; 5: Indoor
29 | 1: Rated Voltage with tolerance; 1: V; 5: 415; 7: ±; 8: 10; 9: % | Link with PR
30 | 1: Frequency with tolerance; 1: Hz; 5: 50; 7: ±; 8: 5; 9: % | Link with PR
31 | 1: No of Phases; 1: -; 5: 3 | Link with PR
32 | 1: TR panel controller type; 1: -; 5: Microcontroller based
33 | 1: TR Panel Incoming Power Supply; 1: -; 5: Common busbar
34 | 1: Method of Pulse control; 1: -; 5: SCR based
35 | 1: Panel make; 1: -; 5: Rittal Panel
36 | 1: Panel Dimensions; 1: -
37 | 1: a) CRCA sheet cubicle thick; 1: mm; 5: Rittal Standard
38 | 1: b) Gland plate; 1: mm; 5: 3.5
39 | 1: c) Doors/covers or Partition plate; 1: mm; 5: 2.5
40 | 1: d) Base channel; 1: mm; 5: 50
41 | 1: e) Panel overall height; 1: mm; 5: < 2100
42 | 1: PCB modules; 2: -; 5: Manufacturer standard
43 | 1: Panel Degree of protection; 1: -; 5: IP 21
44 | 1: Power Supply for Lighting , Power socket and accessories; 1: V; 5: 230
45 | 1: Space heaters; 1: -; 5: Required
46 | 1: Space heater Power supply; 1: V; 5: 230
47 | 1: Incoming cable entry; 1: -; 5: Bottom Entry
48 | 1: Outgoing cable entry; 1: -; 5: Bottom Entry
49 | 1: Mechanical safety Interlock; 1: -; 5: Bracket mounting provision with holes nearer to MCCB
50 | 1: Incoming breaker Type; 1: -; 5: SFU
51 | 1: Incoming breaker rating; 1: Amp; 18: (1)
52 | 1: Panel Input current (Primary current); 1: Amp; 18: (1)
53 | 1: Rapper motor control provisions in TR panel; 1: -; 5: Required
54 | 1: Hazardous certification; 5: Not applicable
55 | 1: CONTROL PANEL INDICATIONS
56 | 1: Primary Current; 1: Amp; 5: Analog meter
57 | 1: Primary voltage; 1: Volt; 5: Analog meter
58 | 1: Secondary voltage; 1: kV; 5: Analog meter
59 | 1: Secondary current; 1: mA; 5: Analog meter
60 | 1: Spark Rate; 1: -; 5: Required
61 | 1: Time Totalizer; 1: -; 5: Required
62 | 1: Lamp Indication (Flush mounted type)
63 | 4: -; 5: Main ON indication (Red Colour); 1: -; 5: Required
64 | 4: -; 5: HT ON indication (Red colour); 1: -; 5: Required
65 | 4: -; 5: Alarm/Trip Indication (Amber colour); 1: -; 5: Required
66 | 4: -; 5: Earth switch close Trip; 1: -; 5: Required
67 | 4: -; 5: Scrapper conveyor Trip; 1: -; 5: Required
68
69
70
71
72
12 | 1: CONTROL PANEL INDICATIONS
13 | 4: -; 5: IGBT Temperature High trip; 1: -; 5: Not Required
14 | 4: -; 5: Phase Fail Indication; 1: -; 5: Required
15 | 4: -; 5: R Phase ON Indication (Red colour); 1: -; 5: Required
16 | 4: -; 5: Y Phase ON Indication (Yellow colour); 1: -; 5: Required
17 | 4: -; 5: B Phase ON Indication (Blue colour); 1: -; 5: Required
18 | 4: -; 5: Phase Unbalance Indication; 1: -; 5: Required
19 | 4: -; 5: SCR Temperature High Trip; 1: -; 5: Required
20 | 4: -; 5: Overload Trip; 1: -; 5: Required
21 | 1: HT ON Pushbutton; 1: -; 5: Required
22 | 1: Heater ON/OFF switch; 1: -; 5: Required
23 | 1: Emergency Push button; 1: -; 5: Required
24 | 1: Local/Remote Selector switch; 1: -; 5: Required
25 | 1: Voltmeter selector switch; 1: -; 5: Required
26 | 1: Ammeter Selector switch; 1: -; 5: Required
27 | 1: Safety Related Signal (SRS signal); 1: -; 5: Not Required
28 | 1: Power OFF rapping provision & its terminals; 1: -; 5: Required
29 | 1: Keypad in TR panels; 1: -; 5: Applicale in any one panel
30 | 1: Interfacing controller /HMI with DCS/PLC; 1: -; 5: Required
31 | 1: Communication to DCS/PLC; 1: -; 5: Ethernet TCP/IP
32 | 1: Hardwired provision with DCS/PLC; 1: -; 5: Suitable terminal blocks, feedbacks and command
33 | 1: -; 5: signals shall be provided by supplier
34 | 1: Gaskets; 1: -; 5: Metal Jacketed Gasket
35 | 1: Panel system earthing; 1: -; 5: 2 no's of earth studs for external earthing
36 | 1: Certification; 1: -; 5: UL
37 | 1: TRANSFORMER RECTIFIER SET ELECTRICAL CHARACTERISTICS
38 | 1: Type; 1: -; 5: Conservator type | Link with PR
39 | 1: Dielectric Fluid; 1: -; 5: Silicon oil as per IEC 836 | Link with PR
40 | 1: Applicable codes and Standards; 1: -; 5: IEC60076, IEC60051, IEC 60529, IEC60255, IEC61439, IEC 60811. IEC 60297, IEC 60947 , Electrical regulation and norm valid in India.
41
42
43 | 1: Rated Voltage with tolerance; 1: V; 5: 415; 7: ±; 8: 10; 9: % | Link with PR
44 | 1: Frequency with tolerance; 1: Hz; 5: 50; 7: ±; 8: 5; 9: % | Link with PR
45 | 1: No of Phases; 1: -; 5: 3 | Link with PR
46 | 1: PCB modules; 1: -; 5: G3 Conformal coating
47 | 1: Installation; 1: -; 5: Outdoor (at ESP roof top)
48 | 1: Primary Current; 1: Amps; 5: 26.4
49 | 1: Secondary voltage; 1: kV (P); 5: 95 | Link with PR
50 | 1: Secondary current; 1: mA; 5: 200 | Link with PR
51 | 1: Marshalling box degree of protection; 1: -; 5: IP 65
52 | 1: Marshalling box gland plate; 1: -; 5: Removable type
53 | 1: TR set cable entry type; 1: -; 5: Bottom Entry with 'C' Type Cu Busbar
54 | 1: TR tank Degree of protection; 1: -; 5: IP 55
55 | 1: Windings; 1: -; 5: Aluminium
56 | 1: Protection device; 1: -
57 | 3: -; 4: Dial Type Thermometer with Alarm & Trip contact; 1: -; 5: Required
58 | 3: -; 4: Level Switch with low alarm contact; 1: -; 5: Required
59 | 3: -; 4: Pressure Switch with high trip contact; 1: -; 5: Required
60 | 3: -; 4: Pressure relief vent; 1: -; 5: Required
61 | 1: Drain valve; 1: -; 5: Required
62 | 1: Sealing arrangement in drain valve (Bottom); 1: -; 5: Required
63 | 1: External HT grounding switch with busduct, limit switches; 1: -; 5: Required
64 | 1: Internal Grounding switch in TR tank; 1: -; 5: Required
65 | 1: Inspection window in grounding switch; 1: -; 5: Required
66 | 1: H.V Bushing; 1: -; 5: Horizontal
67 | 1: Mechanical safety Interlock mounting provision; 1: -; 5: Required
68 | 1: Space heaters in Marshalling box; 1: -; 5: Required
69 | 1: Space heater voltage; 1: V; 5: 110 V AC
70 | 1: Hazardous certification; 1: -; 5: Exe - Increased Safety
71
72
12 | 1: TRANSFORMER RECTIFIER SET ELECTRICAL CHARACTERISTICS
13 | 1: Bolt and Nuts for termination & connections; 1: -; 5: Carbon steel
14 | 1: TR set earthing; 1: -; 5: 2 no's of Earth studs for external earthing
15 | 1: Certification; 1: -; 5: UL
16 | 1: TERMINAL BLOCKS
17 | 1: Terminal block mounting clearance; 1: -; 5: Minimum clearance of 300 mm from gland plate
18 | 1: Incoming & Outgoing Power cable connection; 1: -; 5: Termination with Busbars
19 | 1: Control terminal block type; 1: -; 5: Screw type TB suitable for 4 Sq.mm(max) cables
20 | 1: Voltage grade; 1: -; 5: TB shall be 1100 V Grade
21 | 1: Segregation; 1: -; 5: Power & Control terminal shall be segregated by insulating material like Hylam/Bakelite sheet.
22
23 | 1: Termination; 1: -; 5: Individual insulated sleeves provided for proper termination
24 | 1: INTERNAL WIRING CONNECTIONS
25 | 1: Internal wiring; 1: -; 5: Multistrand PVC insulated copper cable.
26 | 1: Cable dressing; 1: -; 5: Wiring laid in PVC ducts with detachable Snap-on covers.
27 | 1: -; 5: AC 1Ø:Red(L), Black (N), Green with yellow strips (E) AC 3Ø: Red(L1), Yellow(L2), Blue(L3), Black(N) DC Circuit: Red (R), Black(-), Green with yellow strips(E)
28 | 1: Colour code
29
30
31 | 1: Size; 1: -; 5: Power cable size not less than
32 | 5: Control cable size not less than
33 | 5: Instrument cable size not less than
34 | 1: Ferrules; 1: -; 5: Unique duly marked ferrule used for individual wiring.
35 | 1: NAME PLATES & TAG PLATES
36 | 1: Material; 1: -; 5: Stainless steel | Link with PR
37 | 1: Thick; 1: mm; 5: 2 | Link with PR
38 | 1: Font; 1: -; 5: Arial | Link with PR
39 | 1: Inscription engraving with depth; 1: mm; 5: 1.5 | Link with PR
40 | 1: Name plate fixing; 1: -; 5: Fixed with self-threaded screws | Link with PR
41 | 1: Warning & Safety instructions; 1: -; 5: Required | Link with PR
42 | 1: Language for name plates; 1: -; 5: English | Link with PR
43 | 1: Language for warning & safety instructions; 1: -; 5: English | Link with PR
44 | 1: Instructions; 1: -; 5: Insert Harmony logo in Name plates
45 | 1: PAINTING
46 | 1: Panel front & rear paint shade; 1: -; 5: RAL 7035 | Link with PR
47 | 1: End panel sides paint shade; 1: -; 5: RAL 7035 | Link with PR
48 | 1: TR set Paint shade; 1: -; 5: RAL 7035 | Link with PR
49 | 1: QUANTITY
50 | 1: S.no; 4: Description; 16: Tag no's; 5: Rating; 11: Remarks
51 | 1: 1; 4: TR Set & Control panel - Field - 1; 16: Later; 5: 95 kV(P),200 mA
52 | 1: 2; 4: TR Set & Control panel - Field - 2; 16: Later; 5: 95 kV(P),200 mA
53 | 1: 3
54 | 1: 4
55 | 1: 5
56 | 1: 6
57 | 1: 7
58 | 1: 8
59 | 1: 9
60 | 1: 10
61 | 1: 11
62 | 1: 12
63 | 1: 13
64 | 1: 14
65 | 1: 15
66 | 1: 16
67
68
69
70
71
72
12 | 1: FOLLOWING DRAWINGS & DOCUMENTS SHALL BE SUBMITTED BY VENDOR
13
14 | 1: 1. Catalogues
15 | 1: 2. Technical datasheets
16 | 1: 3. General arrangement drawings
17 | 1: 4. Electrical schematic wiring drawings
18 | 1: 5. Bill of materials(BOM)
19 | 1: 6. Recommended list of spares for 2 years
20 | 1: 7. Calculations for input & output power, KVA, Primary current.
21 | 1: 8. Quality assurance plan(QAP)
22 | 1: 9. Mapping address with READ/WRITE parameters.
23 | 1: 10.Preservation procedure
24 | 1: 11. Clause wise Deviation if any
25 | 1: 12. Installation & O & M manual
26
27 | 1: NOTES
28
29 | 1: 1; 2: Control panels shall have rolled edges with gaskets to form dust proof structure. The doors shall have concealed hinges.
30 | 1: 2; 2: The panel shall be rigid, vibration proof and free from bends and twists.
31 | 1: 3; 2: All instruments shall be compensated for temp. errors and factory calibrated to directly read the primary quantities. Means shall be provided for Zero
32 | 1: 4; 2: adjustment without removing or dismantling the instruments.
33 | 1: 5; 2: Exhaust fan with louvers and quality filters shall be provided on control panel front and rear side.
34 | 1: 6; 2: Panel switch gear components shall be accessible from front.
35 | 1: 7; 2: Front/back doors shall be have industrial door locks.
36 | 1: 8; 2: Control panel shall be provided with Surge suppression network , adequately rated RF surge suppressors, filters shall be connected across the
37 | 2: relay coils to avoid interference/harmonics from PLC/DCS system .
38 | 1: 9; 2: Transformer tank shall be weather-proof with welded construction, 4 bi-directional skids, & lifting lugs(top of TR tank)for easy transport and lifting
39 | 1: 10; 2: Burrs and sharp edges on & inside tanks to be removed and maintained smooth.
40 | 1: 11; 2: Core shall be high non aging cold rolled grain oriented silicon sheet steel lamination .
41 | 1: 12; 2: The transformer shall be oil immersed, self cooled type .
42 | 1: 13; 2: The transformer shall be capable of withstanding thermal and mechanical stresses caused by short-circuits on external terminals in
43 | 2: accordance with IEC 60076, symmetrical and asymmetrical faults on any winding
44 | 1: 14; 2: Linear reactors shall be provided on primary side for limiting short circuit current.
45 | 1: 15; 2: Each transformer shall be designed for minimum no-load and load losses within the economic limit as per IEC standards.
46 | 1: 16; 2: The rectifier unit is full wave bridge rectifier. The rectifier comprises of glass sealed silicon diodes having avalanching characteristics.
47 | 1: 17; 2: Minimum 20% spare terminals shall be provided
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64
65
66
67
68
69
70
71
72

## DATAS
Voltage | Tolerance | Frequency | Phases | Installation | Standards | Short ckt capacity | Make | TR Controller Make | kV(p)Rating | mA Rating | Type of control | PCB conformal coating types | Type of panel construction | Construction thickness |  |  |  |  | Control panel IP protection | Power Distributin system | Control supply in panel | Breaker Rating | Breaker Type | Cabel entry | Provision | Space heater Power supply | HV bushing provision | Keypad | Communication | Gaskets | Transformer Type | Oil & Stds | Oil Std | ACCESSORIES | FOR LIFTING | Provision | Controller Type | Name plate material | Name plate thickness | Paint SHADE | Panel Painting process | TR set Painting process | Language | DFT Thickness | Certification | Colour Code | Windings | Hazardous certification
380 | 3 | 50 | 2 | Indoor | IEC60051,IEC 60529, IEC60255, IEC61439, IEC 60811, IEC 60297, IEC 60947 | 45 kA for 1 Sec | Ador/Kraft/Hind Rectifiers/NWL | Precicon- R | 70 | 200 | SCR based | G3 Conformal coating | Rittal Panel | CRCA sheet Cubicle | Gland plate | Door/ covers | Base channel | Height | IP 21 | Individual cable | 110 | 80 | MCCB | Bottom Entry | Required | 230 V AC | Horizontal | Applicable in individual panels | MODBUS- RS485 | PTFE gasket | Hermetically Sealed type | Mineral Oil as per IEC 296 Class I | IEC 296 | Bolts and nuts | Lifting lugs | Required | Microprocessor based | Stainless steel | 2 mm | RAL 1000 | Powder coated , Seven tank process | Sa 2.5 Blasting | English | 80 microns | GOST | Voltage levels shall be identified by a cable colour code as per IS/IEC Standards. | Copper | Exe - Increased Safety
400 | 5 | 100 | 3 | Outdoor | IEC60051, IEC 60529, IEC60255, IEC61439, IEC 60811. IEC 60297, IEC 60947 , Electrical regulation & norm valid in India. | 50 kA for 1 Sec | Ador/Kraft/Hind Rectifiers/NWL/Rico-werk | Precicon-S | 90 | 250 | IGBT based | Silicone conformal coating | Fabricated panel | 1.6 | 3 | 1.6 | 50 | < 2100 | IP 31 | Common busbar | 220 | 100 | SFU | Top Entry | Not Required | 110 V AC | Vertical | Applicale in any one panel | MODBUS TCP/IP | Neoprene gasket | Conservator type | Mineral oil as per IS 335-1993 | IS 335 | Stainless steel | Top of transformer tank | Not required | Microcontroller based | Aluminium Anodised plate | 3 mm | RAL 1001 | Manufacturer Standard | Manufacturer Standard | Vietnamese | 100 microns | EAC | AC 1Ø:Red(L), Black (N), Green with yellow strips (E) AC 3Ø: Red(L1), Yellow(L2), Blue(L3), Black(N) DC Circuit: Red (R), Black(-), Green with yellow strips(E) | Aluminium | Exd - Flameproof protection
415 | 10 |  |  |  |  | 65 kA for 1 Sec | ADOR POWERTRON | Precicon-R3 | 110 | 300 | HFPS | Urethance conformal coating |  | 2 | 3.5 | 2 | 75 | < 2000 | IP 42 |  | 230 | 125 | [6 empty] | PROFIBUS | Rubber gasket |  | Silicon oil as per IEC 836 | IEC 836 | Mild Steel | Both sides of transformer |  |  |  |  | RAL 1002 | Harmony painting standard specification | Harmony painting standard specification | Chinese | 120 microns | CSA |  |  | Exw- Weatherproof
440 | [5 empty] | 100 kA for 1 sec | KRAFT POWERCON | REDKOH CONTROLLER | 120 | 350 |  | Epoxy conformal coating |  | 2.5 | 4 | 2.5 | 100 |  | IP 43 |  | 240 | 160 | [6 empty] | PROFINET | Compressed Non-asbestos Fibre gasket |  |  |  | Carbon steel | [5 empty] | RAL 1003 |  |  | Arabic | 150 microns | UL |  |  | Exn - Non-sparking
460 | [5 empty] | 45 kA for 3 Sec | HIND RECTIFIERS | MK-III Controller |  | 400 |  | Parylene conformal coating |  | 3 | Rittal Standard | Rittal Standard | 150 |  | IP 45 |  |  | 200 | [6 empty] | Ethernet TCP/IP | Spiral Wound gasket | [9 empty] | RAL 1004 |  |  | English & Vietnamese | 180 microns | Not Applicable |  |  | Exi: Intrinsic safety
[6 empty] | 50 kA for 3 Sec | NWL | ACE-16 |  | 450 |  | Conformal coating |  | Rittal Standard |  |  | Rittal Standard |  | IP 54 |  |  | 250 | [7 empty] | Metal Jacketed Gasket | [9 empty] | RAL 1005 |  |  | English & Chinese | 200 microns |  |  |  | Exo: Oil-immersed
[6 empty] | 65 kA for 3 Sec | RICO-WERK | ACE 4 Nextgen |  | 500 |  | Manufacturer standard | [6 empty] | IP 55 |  |  | 315 | [17 empty] | RAL 1006 |  |  | English & Arabic | 250 microns |  |  |  | Exq: Quartz-encapsulated
[6 empty] | 100 kA for 3 sec | Vendor to specify | ADOR Standard Controller |  | 550 | [8 empty] | IP 65 |  |  | 400 | [17 empty] | RAL 1007 |  |  |  | 80-100 microns |  |  |  | Exm: Increased safety for mining
[7 empty] | LATER | Kraft Standard Controller |  | 600 | [11 empty] | 630 | [17 empty] | RAL 1011 |  |  |  | 100-120 microns |  |  |  | Exp: Pressurized
[8 empty] | NWL Controller |  | 650 | [29 empty] | RAL 1012 |  |  |  | 120-150 microns |  |  |  | Exs: Increased safety
[8 empty] | RIECCO MAKE Controller |  | 700 | [29 empty] | RAL 1013 |  |  |  | 150-180 microns |  |  |  | Exv: Vacuum
[8 empty] | PROMETOS- Rico Controller |  | 750 | [29 empty] | RAL 1014 | [7 empty] | Exw: Weatherproof
[8 empty] | Vendor to specify |  | 800 | [29 empty] | RAL 1015 | [7 empty] | Exz: Intrinsically safe for Zone 0 (most hazardous)
[8 empty] | LATER |  | 850 | [29 empty] | RAL 1016 | [7 empty] | Not applicable
[10 empty] | 900 | [29 empty] | RAL 1017
[10 empty] | 950 | [29 empty] | RAL 1018
[10 empty] | 1000 | [29 empty] | RAL 1019
[10 empty] | 1100 | [29 empty] | RAL 1020
[10 empty] | 1200 | [29 empty] | RAL 1021
[10 empty] | 1300 | [29 empty] | RAL 1023
[10 empty] | 1400 | [29 empty] | RAL 1024
[10 empty] | 1500 | [29 empty] | RAL 1026
[10 empty] | 1600 | [29 empty] | RAL 1027
[10 empty] | 1700 | [29 empty] | RAL 1028
[10 empty] | 1800 | [29 empty] | RAL 1032
[10 empty] | 1760 | [29 empty] | RAL 1033
[10 empty] | 2000 | [29 empty] | RAL 1034
RAL 1035
RAL 1036
RAL 1037